## Sheet1
AB 589 flow rate calculations:
Use Bernolli's equation, flow rate is the unknown.
Here is the example from Larry based on data from two postions, the calculated flow rate is compared to flow meter reading
Position 1 input data |  |  |  |  | Position 2 input data
|  |  | meteric units |  |  |  |  | meteric units |  | conv factor | 1 psi=0.70285 m
P1 (psi) | 6.2 |  | 4.3577 | m | P1 (psi) | 0.8 |  | 0.56228 | m |  | 1 ft=0.3048
Z1 (ft) | 0 |  | 0 | m | Z1 (ft) | 12.92 |  | 3.938 | m |  | 1 in=0.0254 m
D1 (in) | 8 |  | 0.2032 | m | D1 (in) | 12 |  | 0.3048 | m |  | 1 gpm= 0.00006309 m^3/s
A1 |  |  | 0.032442 | m^2 | A2 |  |  | 0.072995 | m^2 |  | g=9.81 m/s^2
V1 (m/s) | unknown |  |  |  | V2 (m/s) |  | 0.44444 | of V1
g=9.81 m/s^2
Total energy at point 1 in meters
v1 sq- v2 sq | 2.7983
V1 sq | 5.037
V1 | 2.2443 | m/s | 7.3633 | ft/s
Q | 0.072811 | m^/s
Q | 1154.0819 | gpm